## SL in BTU per hr
Energy Factor Calculator for Commercial DHW Tanks
Developed by David R. Roberts, P.E.
Architectural Energy Corporation
Last updated April 2, 2004
Modified for multifamily by Bruce Harley 2/7/08
Modified to use standby loss in BTU/hr by Brian Stanfill and Kevin Felt 10/12/10
Enter tank size, thermal efficiency and standby loss from GAMA directory
For a single family home, enter 1 in the # dwellings, and the # of bedrooms
For mulitfamily residence, enter the # of apartments and total # of bedrooms served by the hot water heater
Tank size | 119
Thermal Efficiency (%) | 96
Standby Loss (Btu/hr) | 1084
# dwellings | 1
# bedrooms | 3
Energy in daily draw (Btu) | 41242.663
Standby loss (Btu) | 26016
Equivalent Energy Factor | 0.58867
While based on DOE test procedures for storage water heaters, calculations
produce an estimate of an equivalent EF, and not necessarily the exact EF
the test procedures might produce.
DOE Standard Test Conditions
Hot water setpoint (F) | 135
Entering water temperature (F) | 58
Hot water use (gallons/day) | 64.3
Ambient air temperature (F) | 67.5
Calculated automatically
Note: This technique for multifamily adjustments is based on an assumption that the water heating model in the software is simplified (e.g. based on MEPR, or HW usage / EF) and that the efficiency benefits of large-scale usage of water heating equipment are not explicitly modeled in the software. If the software has a more explicit model, it would not be appropriate for the rater to enter values based on this multi-family adjustment.

## SL in % per hr
Energy Factor Calculator for Commercial DHW Tanks
Developed by David R. Roberts, P.E.
Architectural Energy Corporation
Last updated April 2, 2004
Modified for multifamily by Bruce Harley, 2/7/8
Modified to use standby loss in BTU/hr by Brian Stanfill and Kevin Felt 10/12/10
Enter tank size, thermal efficiency and standby loss from GAMA directory or manufacturer's specifications
For a single family home, enter 1 in the # dwellings, and the # of bedrooms
For mulitfamily residence, enter the # of apartments and total # of bedrooms served by the hot water heater
Tank size | 119
Thermal Efficiency (%) | 63
Standby Loss (%) | 1.33
# dwellings | 4
# bedrooms | 8
Energy in daily draw (Btu) | 128282
Standby loss (Btu) | 21357.9034
Equivalent Energy Factor | 0.54008
While based on DOE test procedures for storage water heaters, calculations
produce an estimate of an equivalent EF, and not necessarily the exact EF
the test procedures might produce.
DOE Standard Test Conditions
Hot water setpoint (F) | 135
Entering water temperature (F) | 58
Hot water use (gallons/day) | 200
Ambient air temperature (F) | 67.5
Calculated automatically
Note: This technique for multifamily adjustments is based on an assumption that the water heating model in the software is simplified (e.g. based on MEPR, or HW usage / EF) and that the efficiency benefits of large-scale usage of water heating equipment are not explicitly modeled in the software. If the software has a more explicit model, it would not be appropriate for the rater to enter values based on this multi-family adjustment.